## Slide 1
Combined Cybersecurity and
SIS/SIL Design
MLM-020-A
Industry – Process Industry
Principal Role – All
Professional Role – Control Engineer + Process Engineer
Enterprise Phase – Master Planning
Turn on your audio and click start to begin video
Notes: This MLM provides an example of the use of Cybersecurity and Functional Safety Standards for Automation and Control Systems (ACS) during the Design Phase.
The intended audience is engineers who need an introduction to the interactions between control, safety, and security design requirements.
Click the START button when you are ready to advance to the next slide.

## Slide 2: Key Definitions
Safety
  Freedom from unacceptable risk.
  [SOURCE: IEC 61508-4, 2010, 3.1.11 and IEC 62443-1-1, 2009, 3.2.94]
Functional Safety
  Part of the overall safety relating to the EuC and the EuC Control System that depends on the correct functioning of the E/E/PE safety-related systems and other risk reduction measures. [SOURCE: IEC 61508-4, 2010, 3.1.12]
Conflict between Safety and Security
  A situation where the system cannot achieve its required target performance because one or several safety measures and one or several security countermeasures are not coordinated.
Security
  Condition of system resources being free from unauthorized access and from unauthorized or accidental change, destruction, or loss [SOURCE IEC 62443-1-1]
Notes: Key Definitions include:
SAFETY means freedom from UNACCEPTABLE risk
FUNCTIONAL SAFETY is part of the overall safety relating to the Equipment under Control (or EuC) and the EuC Control System that depends on correct functioning of safety systems and other risk reduction measures.
CONFLICT BETWEEN SAFETY AND SECURITY can arise when one or more safety measures and one or more security countermeasures are uncoordinated, preventing safety measures from achieving their required target performance. Note: Such conflicts can be inherent or unapparent in the defining documentation for a project, and may require redefinition or abandonment.
SECURITY is the condition of system resources being free from unauthorized access and from unauthorized or accidental change, destruction, or loss. Note that measures can be related to physical security (such as controlling physical access to computing assets) or to logical security (the capability to log into a given system and application.) Security has also been defined as:
  the condition of a system that results from the establishment and maintenance of measures to protect the system, or
  The capability of a computer-based system to provide adequate confidence that unauthorized persons and systems can neither modify the software and its data, nor gain access to the system functions, and yet to ensure that this is not denied to authorized persons and systems, or
  prevention of illegal or unwanted penetration of, or interference with, the proper and intended operation of an industrial automation and control system.
Note that the terms “System under Consideration” (or SuC) and “Equipment under Consideration” (or EuC) are commonly used in cybersecurity.

## Slide 3: Source Technical Specification Draft
This MLM is based on the current committee draft of IEC TS 63069 “Framework for Safety and Security” Annex D.
The TS 63069 Technical Specification is intended to interface the two “horizontal” safety and security standards series, IEC 61508 and IEC 62443.
This Technical Specification had an earlier existence as a Technical Report but has been heavily revised to better align with the recent ISA TR84.00.09 (based on IEC/ISA 61511, the process industry domain standard of 61508).
Both IEC 61508 and IEC 62443 standards are currently under revision, so internal references are subject to change.
The contents of the TS are currently purely informative and subject to revision.
Notes:   This MLM is based on the current committee draft of IEC TS 63069 “Framework for Safety and Security” Annex D.
  The TS63069 Technical Specification is intended to interface the two ‘horizontal’ safety and security standards, IEC 61508 and 62443.
  This Technical Specification had an earlier existence as a Technical Report but has been heavily revised to better align with the recent ISA TR84.00.09 (based on IEC/ISA 61511, the process industry domain standard of 61508).
  Both IEC 61508 and IEC 62443 standards are currently under revision, so internal references are subject to change.
  The contents of the TS are currently purely informative and subject to revision.

## Slide 4: Basis of Design
The Project Scope Definition defines what the process is required to do, and constraints on acceptable methods of achieving those objectives.
It can happen that there are unrecognized incompatibilities in the specified requirements that will only become apparent as the design progresses.
Notes: The Project Basis of Design typically defines what the process is required to do, including constraints such as safety, reliability, and cybersecurity requirements.
It can happen, however, that there are unrecognized incompatibilities in the specified requirements that will only become apparent as the design progresses.
Hazard and risk assessment (or H and RA) allows the identification of hazardous events and assessment of risk, for safety-related systems. These requirements form the baseline of the safety strategy for the identified risks.
Cybersecurity requirements, however, ensure that the operational environment, including safety-related systems, provides suitable security countermeasures based on the known threats and vulnerabilities of the system at the time. However, cybersecurity risk evolves as new threats materialize, or new threat vectors and vulnerabilities are exploited, which may lead to the need for revised security countermeasures. However, by contrast, safety requirements remain reasonably stable between modifications to the system.

## Slide 5: General Process of Risk Assessment – Page 1
Process Step adapted from Safety Lifecycle (IEC 61508)
Process Step adapted from Security Risk Analysis (IEC 62443-3-2)
Process Step where co-engineering is recommended
Color Key
Expanded Risk Process
Specification
Identify the System Under Consideration (SuC)
Initial Risk > Tolerable Risk
Safety Hazard and Risk Analysis
Allocation of Safety Functions to Protection Layers
Initial Cybersecurity Risk Assessment
Partition the SuC into Zones and Conduits
Initial Safety Requirements Specification
First Pass Sequence
When:
In the latter stages of Preliminary Engineering
Before cost/time estimates are frozen
Project Scope Definition
Notes: Note that this flowchart has been split in two as the scope does not conveniently fit to a single slide. The initial path flows from top to bottom and then to the following page.
If you are watching this presentation as a video, click the “pause” icon and carefully examine each step in this flowchart.
Click the “play” icon to continue.

## Slide 6: General Process of Risk Assessment – Page 2
Expanded Risk Process
Specification
Identify the System Under Discussion (SuC)
Project Scope Definition (A2)
First Pass Sequence
Initial Risk > Tolerable Risk
NO
NO
Specification
Identify the System Under Discussion (SuC)
Project Scope Definition (A2)
First Pass Sequence
Initial Risk > Tolerable Risk
Detailed Cybersecurity Risk Assessment (DCRA)
Process Step adapted from Safety Lifecycle (IEC 61508)
Process Step adapted from
Security Risk Analysis (IEC 62443-3-2)
Process Step where co-engineering is recommended
Cybersecurity Requirements Specification
and Consolidation with
Safety Requirements Specification
Key
Residual Risk > Tolerable Risk
Requirements Specification (A4)
NO
YES
NO
Specification
Identify the System Under Consideration (SuC)
Project Scope Definition (A2)
First Pass Sequence
Initial Risk > Tolerable Risk
YES
By Whom:
Control System Engineer
Functional Safety Engineer
Cybersecurity Engineer
Process and Operations Specialists
YES
Notes: Continuing from the previous page, this flowchart illustrates the possible need for iterations until the asset owner’s risk criteria are satisfied.
This is accomplished by modifying the design and/or the organizational procedures intended to reduce the risks to tolerable levels.
The modified design is then reevaluated as part of the Detailed Cybersecurity Risk Assessment.
If it is not possible to achieve an acceptable level of security, recycling to the start may be required to modify the envisaged specifications.
Note 1: This is the flow scheme as defined in the TS. A clearer sequence may be detailed.
Note 2: The recycle back to the start is contrary to ISA TR84.00.09 design, which assumes that tolerable risk can always be achieved.

## Slide 7: General Process of Risk Assessment - Initial
Expanded Risk Process
Specification
Identify the System Under Consideration (SuC)
Project Scope Definition
• Functional requirements
• Existing policies & procedures
Inputs
Outputs
• Project scope document
• Preliminary asset inventory
• Responsibilities for IT/OT
• Initial safeguards
• Initial cybersecurity measures
Safety Hazard & Risk Analysis
If an acceptable solution cannot be achieved within specified policies and procedures, reconsider basic inputs.
Notes: Developing the Project Scope (covered in TS 63069 annex D Clause A2) requires the functional requirements and existing corporate policies and procedures, for the System under Consideration (SuC). This also requires a preliminary asset inventory, the proposed split in responsibilities between the Information Technology (IT) group and the Operational Technology (OT) group, initial safeguarding systems, and initial cybersecurity measures.
This Project Scope specifications will then be passed to the Safety Hazard and Risk Analysis.
Note that it is possible for the specification to contain unrecognized incompatibilities, which may not become apparent until the design is further developed.

## Slide 8: General Process of Risk Assessment - Initial
Expanded Risk Process
Inputs
Outputs
• Risk policies and metrics
• System diagrams
• Asset groups and inventory
• Initial safeguards
• Hazards / hazardous events
• Safety functions and safeguards
• System diagrams
• Asset groups and inventory
• Hazards / hazardous events
• Safety functions and safeguards
• Asset groups and inventory updated with safety controllers and assets assigned to safety functions
• System diagrams updated with placement of safety controllers and safety-related assets in the network
• Safety functions and safeguards assigned to layers of protection
• Hazards / hazardous events & worst-case-consequences
Safety Hazard and Risk Analysis
Allocation of Safety Functions to Protection Layers
Initial Cybersecurity Risk Assessment
Identify System under Consideration (SuC)
Notes: Hazard and Risk Analysis (A.3) covers both the Safety and Cybersecurity systems; the Safety Hazard and Risk Analysis requires as inputs Risk Policies and Metrics (both statutory and corporate), System Diagrams, Asset Groups and inventory and initial safeguards for persons, property and the environment.
This study will document foreseen hazards and hazardous events and safety functions and safeguards and will flow forward to the Allocation of Safety Functions to various Protection Layers.
Hazards / hazardous events, Safety functions and safeguards, System diagrams, and Asset groups and Inventory provide the input to the Allocation of Safety Functions to Protection Layers. The outputs from this step will include :
Asset groups and inventory updated with safety controllers and assets assigned to safety functions,
System diagrams updated with placement of safety controllers and safety-related assets in the network,
• Safety functions and safeguards assigned to layers of protection, and
• Hazards / hazardous events & worst-case-consequences.

## Slide 9: General Process of Risk Assessment - Initial
Expanded Risk Process
Initial Cybersecurity Risk Assessment
Partition the SuC into Zones and Conduits
Inputs
Outputs
• Risk policies and metrics
• Purpose & functionality of the SuC
• Major hazards & worst-case consequences
• Purpose/functionality of the SuC
• Geographical location of assets
• Initial risk evaluation
• Operational functions & associated asset groups
• System diagrams
• Initial risk evaluation: worst-case unmitigated risk per operational function/asset group
• Initial SPR-T for operational functions/asset groups (optional)
• Updated Asset inventory with asset groups assigned to zones
• Updated system diagram including zones & conduits
• Data flow diagrams
Allocation of Safety Functions to Protection Layers
Initial Safety Requirements Specification
Notes: Flowing forward from the Safety Functions Allocation we come to the Initial Cybersecurity Risk Assessment. In comparison with safety assessments, this is more fluid in time and likelihood.
Inputs include Corporate risk policies and metrics, the purpose and functionality of the SuC, and perceived major hazards and worst-case consequences that could flow forward from them.
Outputs will be the operational functions and associated asset groups, system diagrams and an initial Security Risk Evaluation based on the worst-case unmitigated risk per operational function or asset group.
This can generate an initial Security Protection Rating target (SPR-T) for each of these groups.
With the purpose and functionality of the SuC determined and geographical location of assets determined, and the Initial Cybersecurity Risk available, the SuC can be divided into Zones of common interest, connected by secured Conduits.
This results in an updated Asset Inventory, with asset groups assigned to Zones, updated system diagrams including the Zones and Conduits, and Data Flow Diagrams.
This provides the input to the Initial Safety Requirements Specification.

## Slide 10: General Process of Risk Assessment - Initial
Expanded Risk Process
Initial Risk > Tolerable Risk
Initial Safety Requirements Specification
Inputs
Outputs
• System diagrams incl. zone and conduit diagrams
• Safety functions and safeguards assigned to layers of protection
• Updated system diagrams including safety-related systems and required data flow
• Initial safety requirements
Partition the SuC into Zones and Conduits
Notes: Having partitioned the System under Consideration into Zones of commonality connected by Conduits, the System Diagrams are available, and the Safety functions and safeguards have been assigned to their layers of protection. These provide the inputs to the Initial Safety Requirements Specification (SRS).
The SRS contains updated system diagrams including safety-related systems, required data flows, and the initial safety requirements.

## Slide 11: General Process of Risk Assessment – cont.
NO
Expanded Risk Process
Detailed Cybersecurity Risk Assessment (DCRA)
Cybersecurity Requirements Specification (CRS)
and Consolidation with
Safety Requirements Specification (SRS)
Residual Risk > Tolerable Risk
NO
Identify the System Under Consideration (SuC)
Risk Assessment - Initial
Initial Risk > Tolerable Risk
Requirements Specification
Outputs
Inputs
• Cybersecurity risk scenarios
• Unmitigated risk and residual risk per risk scenario
• SPR-T for each zone or conduit, function, or system
• Cybersecurity requirements: Design approval or recommendations to further reduce risk
• Purpose / functionality of the SuC: High level use case inc. data flow diagrams, architectural diagrams, zone and conduit diagrams
• Hazards and potential consequences
• Vulnerabilities and common threats for the SuC
• Risk policies and metrics
• Existing security measures for each zone and conduit
• Existing safety functions, safeguards, and initial
safety requirements
YES
Notes: If the Initial Risk is Tolerable, then design can proceed to generation of the Requirements Specification
If the Initial Cybersecurity Risk is greater than the Tolerable Risk, then the Detailed Cybersecurity Risk Assessment (DCRA) is required to determine the sources and the available means to improve the level of risk to tolerable level. If the available tools are inadequate, then reconsideration of the original design criteria is called for. It could be that the project as defined is infeasible or uneconomic.
The Inputs required for the DCRA are listed
• Purpose / functionality of the SuC: High level use case rsp. data flow diagrams, architectural diagrams, zone and conduit diagrams
• Hazards and potential consequences
• Vulnerabilities and common threats for the SuC
• Risk policies and metrics
• Existing security measures for each zone and conduit
• Existing safety functions, safeguards, and initial safety requirements.

## Slide 12: General Process of Risk Assessment – cont.
Expanded Risk Process
Detailed Cybersecurity Risk Assessment (DCRA)
Cybersecurity Requirements Specification (CRS)
and Consolidation with
Safety Requirements Specification (SRS)
Residual Risk > Tolerable Risk
NO
YES
NO
Identify the System Under Consideration (SuC)
Risk Assessment - Initial
Initial Risk > Tolerable Risk
YES
Requirements Specification
Outputs
Inputs
• Consolidated version of all above outputs
• Full list of safety requirements from policies, regulations, and risk assessments
• Full list of cybersecurity requirements from policies,
regulations, and risk assessments and consolidated with safety requirements
• All above outputs, with special focus on
• Initial safety requirements
• Cybersecurity requirements
IF INSOLUBLE
Notes: The product is the REQUIREMENTS SPECIFICATION
The inputs to this are the outputs of all the previous steps, with special focus on the Initial Safety Requirements and the Cybersecurity Requirements.
The Requirements Specification will contain:
A consolidated version of all previous outputs.
A full list of safety requirements from policies, regulations, and risk assessments.
A full list of cybersecurity requirements from policies, regulations, and risk assessments consolidated with safety requirements.

## Slide 13: Key Messages
The following are key messages in this MLM:
Safety and Security are parallel requirements
  But while Designed Safety can be validated and frozen, Security may deteriorate unless patched.
Security improvement must not deteriorate safety requirements
Just because there is no apparent reason why a system should be breached is no defense against an incautious attack on a different target.
Notes: Security failures can allow attack of mechanical and electrical systems as well as control and communication systems – safety-related or not. They can become resident in a system without apparent effect awaiting a trigger event.
Security requirements alter over time, as software flaws are detected and published, or methods of attack are developed to the point that sophisticated methods of attack become available as a service for purchase.
In protecting the system from such attacks, the possibility arises that the safety system may be degraded, such as by slowing the safety response significantly.
Unintended consequences can be more costly than the intended ones – an intended attack on the Ukrainian Financial System through a scheduled user taxation software update escalated to wipe out global shipping database access for every port and ship serviced by one of the major shipping organizations. It also affected systems apparently unassociated such a chocolate factory in Australia (via a parent company in Switzerland).

## Slide 14: Further Information
This MLM has been adapted from two IEC publicly available documents:
IEC PAS 63325 Ed1, ‘Lifecycle Requirements for Functional Safety and Security for ACS’ issued in 2020, and
IEC TR 63069:2019, ‘Industrial-process measurement, control and automation - Framework for functional safety and security’.
These are currently being combined to form an IEC Technical Specification IEC TS 63069 ‘Framework for functional safety and security’.
ISA TR84.00.09, ‘Cybersecurity Related To The Functional Safety Lifecycle’ covers the field in detail and is currently in revision as Ed3. but is limited to systems covered by IEC ISA 61511
Notes: IEC 61508 is a generic standard for functional safety. The derivative IEC standards such as IEC 61511 are required to not contain any clauses contrary to 61508 (many will be more detailed or cover ground that 61508 does not)

## Slide 15: Further Information
Related MLMs
  MLM-042-A, Cyberattacks on Ukraine's Power Grid - Part 1
  MLM-042-B, Cyberattacks on Ukraine's Power Grid - Part 2
  MLM-042-C, Cyber-attacks on Ukraine's Power Grid 2022 - Epilogue (Russian invasion of Ukraine 24 February 2022)
References
  ISA TR84.00.09-2017, ‘Cybersecurity Related To The Functional Safety Lifecycle’
  IEC PAS 63325 Ed1, ‘Lifecycle Requirements for Functional Safety and Security for ACS’
  IEC TR 63069:2019, ‘Industrial-process measurement, control and automation - Framework for functional safety and security.
Please click here to provide feedback on this module
Notes: The related MLMs discuss recent historical examples of failure (or absence) of cybersecurity.
Note that these references are the last ‘official’ versions rather than unapproved revisions.
The feedback link gathers comments and suggestions which will be used by the author in improving this document.
A transcript of this narrative is available (below each presentation slide) on the ISA 99 Workbench

## Slide 16
Author
Ian H. Gibson
Process, Control, and Safety Engineering Consultant
Industrial Chemist, Chemical Engineer, Instrument Engineer, and Functional Safety Engineer, Ian has designed, built, commissioned, operated, maintained, and debugged plants in mineral processing, polymers, oil & gas, and various other industries over the past 60-odd years. He is a Life Senior Member of ISA and Honorable Fellow of IICA (the affiliated Australian organization).
He has served as an Australian Expert on the IEC 61511 Maintenance Team for ten years and as secretary of ISA 99 WG13.
Translating engineering jargon between I&C, process, mechanical, electrical, structural, and piping specialists is his avocation.
Notes: Ian is a Life Senior Member of the ISA and Honorary Fellow of the Australian IICA with over 60 years of experience in Mineral Processing, Oil and Gas, and many other industries.
He was also on the IEC 61511 Process Safety Maintenance Team and is Secretary of the ISA Cybersecurity Education Working Group (ISA 99 WG13), and is also an active member of the Standards Australia committee on the related IEC standards.